## hazus_fragility_and_recovery
component | compon_prefix | damage_state | imt | ds_median | ds_beta | recov_mean | recov_sigma
Water pump | W_WP | Slight | PGA | 0.15 | 0.75 | 0.9 | 0.3
Water pump | W_WP | Moderate | PGA | 0.36 | 0.65 | 3.1 | 2.7
Water pump | W_WP | Extensive | PGA | 0.77 | 0.65 | 13.5 | 10
Water pump | W_WP | Complete | PGA | 1.5 | 0.8 | 35 | 18
Water tank | W_T | Slight | PGA | 0.18 | 0.5 | 1.2 | 0.4
Water tank | W_T | Moderate | PGA | 0.55 | 0.5 | 3.1 | 2.7
Water tank | W_T | Extensive | PGA | 1.15 | 0.6 | 93 | 85
Water tank | W_T | Complete | PGA | 1.5 | 0.6 | 155 | 120
ESSL substation | P_TF | Slight | PGA | 0.15 | 0.7 | 1 | 0.5
ESSL substation | P_TF | Moderate | PGA | 0.29 | 0.55 | 3 | 1.5
ESSL substation | P_TF | Extensive | PGA | 0.45 | 0.45 | 7 | 3.5
ESSL substation | P_TF | Complete | PGA | 0.9 | 0.45 | 30 | 15
External grids | P_EG | Slight | PGA | 0.11 | 0.5 | 1 | 0.5
External grids | P_EG | Moderate | PGA | 0.15 | 0.45 | 3 | 1.5
External grids | P_EG | Extensive | PGA | 0.2 | 0.35 | 7 | 3.5
External grids | P_EG | Complete | PGA | 0.47 | 0.4 | 30 | 15
Power Line | P_L | Slight | PGA | 0.28 | 0.3 | 0.3 | 0.2
Power Line | P_L | Moderate | PGA | 0.4 | 0.2 | 1 | 0.5
Power Line | P_L | Extensive | PGA | 0.72 | 0.15 | 3 | 1.5
Power Line | P_L | Complete | PGA | 1.1 | 0.15 | 7 | 3
Switch | P_S | Slight | PGA | 0.28 | 0.3 | 0.3 | 0.2
Switch | P_S | Moderate | PGA | 0.4 | 0.2 | 1 | 0.5
Switch | P_S | Extensive | PGA | 0.72 | 0.15 | 3 | 1.5
Switch | P_S | Complete | PGA | 1.1 | 0.15 | 7 | 3
Roads | T_L | Slight | PGD | 12 | 0.7 | 0.9 | 0
Roads | T_L | Moderate | PGD | 24 | 0.7 | 2.2 | 1.8
Roads | T_L | Extensive | PGD | 60 | 0.7 | 21 | 16
Pipe | W_P | Moderate | RR | 0.1 | 1.5 | 0.3 | 0
Pipe | W_P | Extensive | RR | 0.5 | 1.5 | 0.3 | 0
Pipe Main | W_PMA | Moderate | RR | 0.1 | 1.5 | 0.3 | 0
Pipe Main | W_PMA | Extensive | RR | 0.5 | 1.5 | 0.3 | 0

## moderate
component | compon_prefix | damage_state | imt | ds_median | ds_beta | recov_mean | recov_sigma | Remarks
Water pump | W_WP | Slight | PGA |  |  | 0.9 | 0.3
Water pump | W_WP | Moderate | PGA |  |  | 3.1 | 2.7
Water pump | W_WP | Extensive | PGA |  |  | 13.5 | 10
Water pump | W_WP | Complete | PGA |  |  | 35 | 18
Water tank | W_T | Slight | PGA |  |  | 1.2 | 0.4
Water tank | W_T | Moderate | PGA |  |  | 3.1 | 2.7
Water tank | W_T | Extensive | PGA |  |  | 93 | 85
Water tank | W_T | Complete | PGA |  |  | 155 | 120
ESSL substation | P_TF | Slight | PGA |  |  | 1 | 0.5
ESSL substation | P_TF | Moderate | PGA |  |  | 3 | 1.5
ESSL substation | P_TF | Extensive | PGA |  |  | 7 | 3.5
ESSL substation | P_TF | Complete | PGA |  |  | 30 | 15
External grids | P_EG | Slight | PGA |  |  | 1 | 0.5
External grids | P_EG | Moderate | PGA |  |  | 3 | 1.5
External grids | P_EG | Extensive | PGA |  |  | 7 | 3.5
External grids | P_EG | Complete | PGA |  |  | 30 | 15
Power Line | P_L | Slight | PGA |  |  | 0.3 | 0.2
Power Line | P_L | Moderate | PGA |  |  | 1 | 0.5
Power Line | P_L | Extensive | PGA |  |  | 3 | 1.5
Power Line | P_L | Complete | PGA |  |  | 7 | 3
Switch | P_S | Slight | PGA |  |  | 0.3 | 0.2
Switch | P_S | Moderate | PGA |  |  | 1 | 0.5
Switch | P_S | Extensive | PGA |  |  | 3 | 1.5
Switch | P_S | Complete | PGA |  |  | 7 | 3
Roads | T_L | Slight | PGD |  |  | 0.9 | 0
Roads | T_L | Moderate | PGD |  |  | 2.2 | 1.8
Roads | T_L | Extensive | PGD |  |  | 21 | 16
Pipe | W_P | Moderate | RR | 0.1 | 1.5 | 0.3 | 0
Pipe | W_P | Extensive | RR | 0.5 | 1.5 | 0.3 | 0
Pipe Main | W_PMA | Moderate | RR | 0.1 | 1.5 | 0.3 | 0
Pipe Main | W_PMA | Extensive | RR | 0.5 | 1.5 | 0.3 | 0

## low
component | compon_prefix | damage_state | imt | ds_median | ds_beta | recov_mean | recov_sigma | Remarks
Water pump | W_WP | Slight | PGA | 0.2 | 0.4 | 0.9 | 0.3 | Medium Water Treatment Plants (PWTM) with unanchored subcomponents
Water pump | W_WP | Moderate | PGA | 0.35 | 0.4 | 3.1 | 2.7
Water pump | W_WP | Extensive | PGA | 0.75 | 0.5 | 13.5 | 10
Water pump | W_WP | Complete | PGA | 1.28 | 0.5 | 35 | 18
Water tank | W_T | Slight | PGA | 0.15 | 0.6 | 1.2 | 0.4 | On-Ground Wood Tank (PSTGW)
Water tank | W_T | Moderate | PGA | 0.4 | 0.6 | 3.1 | 2.7
Water tank | W_T | Extensive | PGA | 0.7 | 0.7 | 93 | 85
Water tank | W_T | Complete | PGA | 0.9 | 0.7 | 155 | 120
ESSL substation | P_TF | Slight | PGA | 0.1 | 0.6 | 1 | 0.5 | Medium voltage substations (ESSM) with unanchored/standard components
ESSL substation | P_TF | Moderate | PGA | 0.2 | 0.5 | 3 | 1.5
ESSL substation | P_TF | Extensive | PGA | 0.3 | 0.4 | 7 | 3.5
ESSL substation | P_TF | Complete | PGA | 0.5 | 0.4 | 30 | 15
External grids | P_EG | Slight | PGA | 0.09 | 0.5 | 1 | 0.5 | High voltage substations (ESSH) with unanchored/standard components (ESS6)
External grids | P_EG | Moderate | PGA | 0.13 | 0.4 | 3 | 1.5
External grids | P_EG | Extensive | PGA | 0.17 | 0.35 | 7 | 3.5
External grids | P_EG | Complete | PGA | 0.38 | 0.35 | 30 | 15
Power Line | P_L | Slight | PGA | 0.24 | 0.25 | 0.3 | 0.2 | Unanchored/Standard Components (EDC)
Power Line | P_L | Moderate | PGA | 0.33 | 0.2 | 1 | 0.5
Power Line | P_L | Extensive | PGA | 0.58 | 0.15 | 3 | 1.5
Power Line | P_L | Complete | PGA | 0.89 | 0.15 | 7 | 3
Switch | P_S | Slight | PGA | 0.24 | 0.25 | 0.3 | 0.2
Switch | P_S | Moderate | PGA | 0.33 | 0.2 | 1 | 0.5
Switch | P_S | Extensive | PGA | 0.58 | 0.15 | 3 | 1.5
Switch | P_S | Complete | PGA | 0.89 | 0.15 | 7 | 3
Roads | T_L | Slight | PGD | 6 | 0.7 | 0.9 | 0
Roads | T_L | Moderate | PGD | 12 | 0.7 | 2.2 | 1.8
Roads | T_L | Extensive | PGD | 24 | 0.7 | 21 | 16
Pipe | W_P | Moderate | RR | 0.1 | 1.5 | 0.3 | 0
Pipe | W_P | Extensive | RR | 0.5 | 1.5 | 0.3 | 0
Pipe Main | W_PMA | Moderate | RR | 0.1 | 1.5 | 0.3 | 0
Pipe Main | W_PMA | Extensive | RR | 0.5 | 1.5 | 0.3 | 0

## high
component | compon_prefix | damage_state | imt | ds_median | ds_beta | recov_mean | recov_sigma | Remarks
Water pump | W_WP | Slight | PGA | 0.37 | 0.4 | 0.9 | 0.3 | Medium Water Treatment Plants (PWTM) with anchored subcomponents
Water pump | W_WP | Moderate | PGA | 0.52 | 0.4 | 3.1 | 2.7
Water pump | W_WP | Extensive | PGA | 0.73 | 0.5 | 13.5 | 10
Water pump | W_WP | Complete | PGA | 1.28 | 0.5 | 35 | 18
Water tank | W_T | Slight | PGA | 0.18 | 0.5 | 1.2 | 0.4 | Above-Ground Steel Tank (PSTAS)
Water tank | W_T | Moderate | PGA | 0.55 | 0.5 | 3.1 | 2.7
Water tank | W_T | Extensive | PGA | 1.15 | 0.6 | 93 | 85
Water tank | W_T | Complete | PGA | 1.5 | 0.6 | 155 | 120
ESSL substation | P_TF | Slight | PGA | 0.15 | 0.6 | 1 | 0.5 | Medium voltage substations (ESSM) with anchored/seismic components (ESSM)
ESSL substation | P_TF | Moderate | PGA | 0.25 | 0.5 | 3 | 1.5
ESSL substation | P_TF | Extensive | PGA | 0.35 | 0.4 | 7 | 3.5
ESSL substation | P_TF | Complete | PGA | 0.7 | 0.4 | 30 | 15
External grids | P_EG | Slight | PGA | 0.11 | 0.5 | 1 | 0.5 | High voltage substations (ESSH) with anchored/seismic components (ESSH)
External grids | P_EG | Moderate | PGA | 0.15 | 0.45 | 3 | 1.5
External grids | P_EG | Extensive | PGA | 0.2 | 0.35 | 7 | 3.5
External grids | P_EG | Complete | PGA | 0.47 | 0.4 | 30 | 15
Power Line | P_L | Slight | PGA | 0.28 | 0.3 | 0.3 | 0.2 | Anchored/Seismic Components (EDC)
Power Line | P_L | Moderate | PGA | 0.4 | 0.2 | 1 | 0.5
Power Line | P_L | Extensive | PGA | 0.72 | 0.15 | 3 | 1.5
Power Line | P_L | Complete | PGA | 1.1 | 0.15 | 7 | 3
Switch | P_S | Slight | PGA | 0.28 | 0.3 | 0.3 | 0.2
Switch | P_S | Moderate | PGA | 0.4 | 0.2 | 1 | 0.5
Switch | P_S | Extensive | PGA | 0.72 | 0.15 | 3 | 1.5
Switch | P_S | Complete | PGA | 1.1 | 0.15 | 7 | 3
Roads | T_L | Slight | PGD | 12 | 0.7 | 0.9 | 0
Roads | T_L | Moderate | PGD | 24 | 0.7 | 2.2 | 1.8
Roads | T_L | Extensive | PGD | 60 | 0.7 | 21 | 16
Pipe | W_P | Moderate | RR | 0.1 | 1.5 | 0.3 | 0
Pipe | W_P | Extensive | RR | 0.5 | 1.5 | 0.3 | 0
Pipe Main | W_PMA | Moderate | RR | 0.1 | 1.5 | 0.3 | 0
Pipe Main | W_PMA | Extensive | RR | 0.5 | 1.5 | 0.3 | 0